BOULDER GARDENS

FIELDSTATION WORKBOOK

Observations • systems • photographs • source records

MASTER SOURCE OF TRUTH

Field reports are derived from this workbook.
Original evidence remains attached to the record.

Started July 31, 2026
Version 0.4

# How this workbook is used

This workbook is the permanent working record for Boulder Gardens Fieldstation. It keeps observations, equipment details, photographs, instrument readings, calculations, uncertainties, corrections, and later changes together in one place.

Public Field Reports are shorter observational extracts made from these source records. The workbook may contain more technical detail, unfinished questions, and evidence than appears publicly.

| CONFIRMED | Visible in a source image, instrument reading, equipment label, or primary record. |
| --- | --- |
| RECORDED | Previously supplied by Robert and retained as part of the project record. |
| CALCULATED | Derived directly from confirmed or recorded numbers. |
| TO VERIFY | Useful working information that still needs a photograph, label, measurement, or correction. |

## Archive layers

Workbook: Curated source records and cross-references.

Immich: Original photographs and photograph metadata.

GitHub: Website source, Field Reports, and version history.

Local backup: A copy of the workbook, sources, and published site outside the active working folder.

## Record naming

Field Report source records use the form FR001, FR002, and so on. Source files begin with the same identifier so images and notes remain attached to the correct record.

# Workbook index

| Record | Subject | Status | Date |
| --- | --- | --- | --- |
| FR001 | Fieldstation Solar System | Source record opened | 2026-07-31 |

## Planned workbook divisions

01 — Field Report source records

02 — Solar and energy

03 — Water systems

04 — Communications and Meshtastic

05 — Sensors, ESPHome, and Home Assistant

06 — Network and PoE infrastructure

07 — Buildings, land, and access

08 — People, history, and community

09 — Maps, diagrams, and equipment records

10 — Revision log and unresolved questions

The divisions will grow as evidence is collected. A record may be indexed in more than one division without duplicating its source material.

# FIELD REPORT SOURCE RECORD 001

Fieldstation Solar System

| Record ID | FR001 | Record status | Open |
| --- | --- | --- | --- |
| Observation date | July 31, 2026 | Instrument time | 4:10 PM |
| Location | Command Center | Observer | Robert Redecker |
| Subjects | Solar • battery • infrastructure | Public report | Published as Field Report 001 |

## Record scope

This first source record begins with the working photovoltaic and battery system serving the Command Center. It is intentionally limited to what has already been observed or recorded. PoE, Meshtastic, remote sensors, Home Assistant, and related infrastructure will be linked later as separate observations.

## Core observations

[CONFIRMED] The present working photovoltaic array consists of six Talesun TP6F72M(H)-395 modules rated 395 watts each.

[CALCULATED] Present photovoltaic nameplate capacity is 2,370 watts, or 2.37 kW.

[CONFIRMED] Talesun module label values: Voc 48.9 V; Isc 10.35 A; Vmpp 40.3 V; Impp 9.81 A; maximum series fuse 20 A; maximum system voltage 1500 VDC.

[RECORDED] The battery bank consists of sixteen LiFePO₄ cells connected in series.

[CONFIRMED] Cell rating is 3.2 V and 280 Ah; the cell label was photographed on August 8, 2026.

[CALCULATED] Nominal pack voltage is 51.2 V.

[CALCULATED] Nominal stored energy is approximately 14.3 kWh.

[CONFIRMED] Inverter/charger: Schneider Electric Conext XW Pro 6848 NA, part 865-6848-21. The equipment label shows 48.0 V nominal DC output, 6.8 kVA maximum continuous inverter output at 120/240 V, and manufacture date 26 Sep 2022.

[CONFIRMED] Solar charge controller: OutBack FLEXmax 60, model FM60-150VDC. Equipment-label limits include 150 VDC maximum PV open-circuit voltage and a 15–145 VDC nominal operating PV range.

[CALCULATED / CAUTION] Three confirmed Talesun modules in series have 146.7 V open-circuit voltage at STC (3 × 48.9 V). This is already above the controller’s 145 V nominal operating range and only 3.3 V below its 150 V maximum. Because PV Voc increases as module temperature falls, a three-module string can exceed the controller limit in cold conditions. Treat the presently reported 3S2P arrangement as a known risk until physically verified and corrected.

[CONFIRMED] The JK-BMS application displayed a configured capacity of 270.0 Ah at the time of observation.

# Instrument observation: JK-BMS

The following values were transcribed directly from the Android JK-BMS display supplied for this record.

| Observed field | Reading | Record status |
| --- | --- | --- |
| State of charge | 79% | CONFIRMED |
| Pack voltage | 53.48 V | CONFIRMED |
| Current | −1.73 A | CONFIRMED |
| Power | 92.5 W | CONFIRMED |
| Operating state | Discharging | CONFIRMED |
| Estimated time remaining | 123 h 26 min 33 sec | CONFIRMED |
| Configured capacity | 270.0 Ah | CONFIRMED |
| Remaining capacity | 213.4 Ah | CONFIRMED |
| Highest cell | 3.344 V | CONFIRMED |
| Lowest cell | 3.342 V | CONFIRMED |
| Displayed voltage difference | 0.004 V | CONFIRMED |
| Balancing current | 0.000 A | CONFIRMED |
| Highest reported temperature | 39.0 °C | CONFIRMED |
| Cell type | LFP | CONFIRMED |
| Charge control | ON | CONFIRMED |
| Discharge control | ON | CONFIRMED |
| Balancing | OFF | CONFIRMED |

The application displayed a 0.004 V pack spread while the displayed high and low values differ by 0.002 V. Both values are preserved exactly as shown rather than reconciled.

# Source image FR001-S01

FR001-S01. JK-BMS Android status screen at 4:10 PM on July 31, 2026. Original source file preserved in the companion sources folder.

# Calculated values

| Quantity | Inputs | Calculation | Result |
| --- | --- | --- | --- |
| Present PV nameplate | 6 modules × 395 W | 6 × 395 | 2,370 W / 2.37 kW |
| Nominal battery voltage | 16 cells × 3.2 V | 16 × 3.2 | 51.2 V |
| Nominal battery energy | 51.2 V × 280 Ah | 51.2 × 280 | 14,336 Wh / 14.3 kWh |
| Configured BMS energy | 51.2 V × 270 Ah | 51.2 × 270 | 13,824 Wh / 13.8 kWh |

## Equipment inventory

| Component | Recorded identification | Status | Evidence needed |
| --- | --- | --- | --- |
| PV modules | 6 × Talesun TP6F72M(H)-395, 395 W each | CONFIRMED | FR001-S08 panel label |
| Inverter | Schneider Electric Conext XW Pro 6848 NA, part 865-6848-21 | CONFIRMED | FR001-S11 equipment label |
| Charge controller | OutBack FLEXmax 60, FM60-150VDC | CONFIRMED | FR001-S10 equipment label; string wiring still to verify |
| Battery cells | 16 × LiFePO₄, 3.2 V, 280 Ah | CONFIRMED | FR001-S09 cell label; complete bank photograph still useful |
| Battery management | JK smart BMS, 16S application display | PARTLY CONFIRMED | BMS unit label and wiring photograph |
| Protection | Disconnects, breakers, and Class-T protection previously recorded | TO VERIFY | Full electrical-wall photograph and ratings |

## Photographs still needed

Complete sixteen-cell battery bank

PV combiner/string wiring and protection labels

JK-BMS unit, sensing leads, and connector labels

FR001-S07 — disconnects, breakers, and battery protection

## Unresolved questions

How should the present PV strings be reconfigured or otherwise protected so cold-weather open-circuit voltage stays safely within the FLEXmax 60 input limit?

How are the six modules presently wired and protected? Earlier notes indicate two strings of three; this needs visual confirmation. With the confirmed 48.9 V module Voc, three modules in series would total 146.7 V at STC, so actual string wiring and the charge-controller voltage limit must be verified.

What loads were active at 4:10 PM when the BMS reported 92.5 W of discharge?

Which temperature sensor produced the 39.0 °C high-temperature value, and where is it mounted?

The JK-BMS is currently configured for 270 Ah while the cells are confirmed at 280 Ah. Recommended next step: change only the BMS capacity parameter to 280 Ah, leave voltage/current protection settings unchanged, and allow SOC to re-synchronize on a normal full charge.

# Field Report derivation sheet

This section identifies what may safely be extracted for a public Field Report without turning the report into an explanation or tutorial.

| Suitable public observation | Source |
| --- | --- |
| Six 395-watt Talesun modules form the present working array. | Confirmed equipment label |
| The array’s present nameplate capacity is 2.37 kW. | Direct calculation |
| The battery bank contains sixteen LiFePO₄ cells. | Recorded system information |
| At 4:10 PM the pack read 53.48 V and 79% state of charge. | FR001-S01 |
| The system was discharging at 1.73 A / 92.5 W. | FR001-S01 |
| Charging and discharging were enabled; balancing was inactive. | FR001-S01 |
| The BMS displayed 213.4 Ah remaining and a 39.0 °C high temperature. | FR001-S01 |

## Editorial rule for Field Reports

Observe first. Preserve exact readings. Keep interpretation brief. Do not explain general solar theory unless a later report is specifically created for that purpose.

## Revision log

| Version | Date | Change | Status |
| --- | --- | --- | --- |
| 0.1 | 2026-07-31 | Workbook created; FR001 opened; JK-BMS screenshot and readings attached. | Superseded |
| 0.2 | 2026-08-03 | Five additional photographs cataloged; FR001 website captions and image sequence recorded. | Superseded |
| 0.3 | 2026-08-08 | Corrected PV modules to confirmed Talesun 395 W labels; array total corrected to 2.37 kW; 280 Ah cell rating confirmed; system name updated. | Superseded |
| 0.4 | 2026-08-08 | Added OutBack FLEXmax 60 and Schneider Conext XW Pro equipment-label evidence; confirmed controller PV limits; documented 3-module-string cold-weather overvoltage risk; recommended BMS capacity setting correction from 270 Ah to 280 Ah. | Current |

## Next update

Add the remaining wiring/protection photographs, verify the present array series/parallel topology, correct the JK-BMS capacity setting to 280 Ah, and preserve the cold-weather PV-voltage concern in the living record. Field Report 001 is already published; future public corrections should be derived from this workbook.

# FR001 photographic source update

Photographic source record · updated through August 8, 2026

Additional photographs have been supplied and cataloged for Field Report 001, including equipment-label evidence. Original files are preserved in the companion sources/fr001 folder. The public webpage uses optimized copies and concise captions.

| Source | Date | Observed content | Public use |
| --- | --- | --- | --- |
| FR001-S02 | 2025-09-01 | Robert beside the open Schneider inverter while work is underway. | Report hero |
| FR001-S03 | 2026-01-31 | Wide view of panels and the surrounding working area. | The setting |
| FR001-S04 | 2026-07-25 | Ground-mounted modules leading toward the equipment enclosure. | Array and shelter |
| FR001-S05 | 2026-07-25 | Open wooden equipment shelter beside the array. | Equipment shelter |
| FR001-S06 | 2026-07-26 | Several fixed panel mounts below the boulder formations. | Panels among the boulders |
| FR001-S08 | 2026-08-08 | Talesun TP6F72M(H)-395 module label confirming 395 W rating and electrical specifications. | Technical source record |
| FR001-S09 | 2026-08-08 | LiFePO₄ cell label confirming 3.2 V, 280 Ah rating. | Technical source record |
| FR001-S10 | 2026-08-08 | OutBack FLEXmax 60 FM60-150VDC label confirming 150 VDC maximum PV Voc and 15–145 VDC nominal operating range. | Technical source record |
| FR001-S11 | 2026-08-08 | Schneider Electric Conext XW Pro 6848 NA inverter/charger label, part 865-6848-21, manufactured 26 Sep 2022. | Technical source record |

The setting photographs document visible arrangement. Equipment-label photographs FR001-S08 through FR001-S11 now confirm the PV module, battery-cell, charge-controller, and inverter/charger identifications. Wiring topology and protection details still require direct verification.

## FR001-S02

FR001-S02. Robert beside the open Schneider inverter while work is underway.

## FR001-S03

FR001-S03. Wide view of ground-mounted panels and the surrounding working area.

## FR001-S04

FR001-S04. Ground-mounted modules leading toward the compact equipment enclosure.

## FR001-S05

FR001-S05. Open wooden equipment shelter beside the array.

## FR001-S06

FR001-S06. Several fixed panel mounts below the surrounding boulder formations.

## Remaining photographic needs

Complete battery bank

JK-BMS hardware and sensing leads

PV combiner/string wiring and protection labels

Full electrical protection and disconnect arrangement

## FR001-S10

FR001-S10. OutBack FLEXmax 60 charge-controller equipment label. Model FM60-150VDC; maximum PV open-circuit voltage 150 VDC; nominal operating PV range 15–145 VDC. Photograph supplied August 8, 2026.

## FR001-S11

FR001-S11. Schneider Electric Conext XW Pro 6848 NA inverter/charger equipment label, part 865-6848-21, manufactured 26 Sep 2022. Photograph supplied August 8, 2026.

## Version 0.4 correction note

August 8, 2026 — OutBack FLEXmax 60 and Schneider Conext XW Pro 6848 NA model labels were added as source evidence. The controller voltage limits are now confirmed. The previously reported three-module series string would be 146.7 V Voc at STC, leaving insufficient cold-weather margin below the 150 V controller maximum. The JK-BMS capacity setting of 270 Ah is retained as a historical observation; 280 Ah is now the recommended configured capacity because the cell labels confirm 280 Ah nominal capacity.